## 2ND QRTR 07
GROUP WATER SCHEMES SERVICE INDICATORS 3RD QUARTER (JULY - SEPT INCL) 2007
SCHEME | NO OF TESTS | NUMBER OF COMPLIANT RESULTS | NUMBER NON COMPLIANT RESULTS | %AGE COMP RESULTS | %AGE NON COMP RESULTS | Reason
REAGHSTOWN/KILLANY | 1 | 1 | 0 | 100 | 0
SHEEPGRANGE | - | - | - | - | -
DRYBRIDGE/WATERUNDER | 2 | 2 | 0 | 100 | 0
TULLYALLEN | 3 | 2 | 1 | 67 | 33 | 16/07/07 - Water tested at Gibtex which showed 2 total and 1 faecal coliform. GWS confirmed that these premises are not supplied directly from the Tullyallen supply. Therefore, this sample was not counted.
18/07/07 - Water re-tested at Pat Tuite's house and test was clear.
13/08/07 - Water tested at Pat Tuite's at an outside tap which was not used for some time (78 total and 70 faecal). Therefore, this sample was not counted.
16/08/07 - Water re-tested at P Tuite's (1 total and 1 faecal) and at J Murphy's (18 total & 4 faceal) which resulted in a test failure. Refurbishment works were being carried out at reservoir by group which may have impacted on water quality. 'Notice to boil' put in place.
30/08/07 - Water re-tested at P Tuites, J Gargan's and P Winters and tests were clear.
GRANGEBELLEW | - | - | - | - | -
TENURE | - | - | - | - | - | Ongoing water quality issue from previous quarter. Testing procedure is currently under review.
MOUNTAIN PARK | - | - | - | - | -
ARDAGHY | 1 | 0 | 1 | 0 | 100 | Ongoing problems regarding disinfection with this scheme despite upgrading works having been carried out. LCC has written to DOEHLG for their recommendation in this case.
BALLYMAKENNY | 2 | 1 | 1 | 50 | 50 | 16/07/07 - Water tested at Fay's (6 total & 2 faecal). Group advised to increase chlorine levels and scour network.
03/08/07 - Water re-tested at T O'hEochaidh's & A McQuillans which was <10 total.
TOTAL | 9 | 6 | 3 | 67 | 33
-